## Sheet1
TECHNICAL DATASHEET - ELECTRICAL
FF Electrical Pump SCFP-F-125/390-1000-M/E-/Splitcase/50/UL/FM - Splitcase
SELECTION CRITERIA
Article Number | 68331049
Flow(GPM) | 1000 | Approval | UL/FM
Pressure(Bar) | 13 | Frequency | 50
Speed (RPM) | 2900
PUMP MATERIAL OF CONSTRUCTION
Casing | Cast Iron | Shaft | Alloy Steel
Impeller | Bronze | Flange Size (inch) | 8X5
Flange Class (Suction;Discharge) | ANSI B16.1,Class250
ELETRICAL MOTOR
Rating (HP) | 200 | Voltage | 400
Operation | 3 phase | Type | ODP
Frequency | 50 | Approval | UL
Motor/Engine model | - | Brand | Hitec/Marathon
Make | UK/USA | Country of Origin | China
CONTROL PANEL
Enclosure Type | NEMA2 | Controller Model | GPY-200
Voltage/Frequency | 400 | Approval | UL/FM
STANDARD ACCESSORIES
SPLIT CASE PUMP
Casing Relief Valve | Zurn/AGF/Watts- Brand is Factory Choice*subjects to availability
Suction Pr.Gauge | HDPG 1130A or Equivalent
Discharge Pr. Gauge | Type 711/Amekai/China Or Equivalent
Air Release valve*(for splitcase pumps only) | WEFLOW/eqv-for upto 200 Psi rating pumps WEFLOW -for upto 300 Psi rating pumps*subjects to availability
ENDSUCTION PUMP
Casing Relief Valve | Zurn/AGF/Watts- Brand is Factory Choice*subjects to availability
Suction Pr.Gauge | HDPG 1130A or Equivalent
Discharge Pr. Gauge | Type 711/Amekai/China Or Equivalent
GENERAL OPERATION CONDITION
Parameters | Conditions Considered
Water Type | Fresh Water*
Water Temperature | 5 to 49 Degree celsius
Altitude | Upto 300 feet above Sea level*
Ambient Temperature | 5 to 25 Degree Celsius
Suction State | Totally Flooded Suction*
Standard Selection of Electric Motor Type will Be ODP. Standard Selection of Starter Type will be DOL for motor rating upto 75 HP . Standard Star Delta Open Transition type for motors ratings greater than 75 HP. Standard Selection of Controllers Enclosure Rating will be Nema 2-IP31.
Notes:* | For higher altitude & higher ambient temperatures- deration factors to be considered on drivers.
For lesser NPSHa with respect to NPSHr @ actual site conditions.
Sea water/Saline water/ water with higher TDS values.
For such cases please contact Wilo engineering for assistance