## Sheet1
Technical Datasheet - Diesel Wilo logo
NFP-F-80/278-500-M/E/End suction/50/60/UL/FM - End suction
Pump image
Pump Article number
Flow(GPM) | 500 |  | Approval | UL/FM
Pressure(Bar) | 9.37 |  | Frequency | 50/60
Speed (RPM) | 2900
Material of construction
Casing | - |  | Shaft | -
Impeller | - |  | Flange Size (inch) | -
Flange Class (Suction;Discharge) | -
Engine paramter
Rating (HP)** | - |  | Voltage | 220
Operation |  |  | Type | Liquid Cooled IC Diesel Engine
Frequency | - |  | Approval | UL
Motor/Engine model | BS04075MSF |  | Brand | Black Stallion
Make | UAE |  | Make | UAE
Diesel Controller
Enclosure Type |  |  | Controller Model** | GPD-12V
Voltage/Frequency | 220/50/60 |  | Approval | UL/FM
Standard Accessories
Split case
Casing Relief Valve | Zurn/AGF/Watts- Brand is Factory Choice*subjects to availability
Suction Pr.Gauge | HDPG 1130A/UAE or Equivalent
Discharge Pr. Gauge | Type 711/Amekai/China Or Equivalent
Air Release valve*(for splitcase pumps only) | WEFLOW/eqv-for upto 200 Psi rating pumps WEFLOW -for upto 300 Psi rating pumps*subjects to availability
End suction pump
Casing Relief Valve | Zurn/AGF/Watts- Brand is Factory Choice*subjects to availability
Suction Pr.Gauge | HDPG 1130A/UAE or Equivalent
Discharge Pr. Gauge | Type 711/Amekai/China Or Equivalent
Diesel Tank (US)-Gallons | 90 | Brand:Wilo/Origin: UAE | Non- Listed
Optonal Accessories
Battery Rating | 100Ah | *Brand will be Factory Choice-Based On Availability
Battery Quantities
Flow Meter (Model G) | 6" | Brand :Gerand; Origin : USA
Pr.Releif Valve (ZW205 series) |  | Brand : Zurn ; Origin: USA
Waste Cone |  | Brand : Wilo ; Origin: UAE
Terminal Box | - | Brand : Wilo ; Origin: UAE
Operating condition
S.no | Parameters | Conditions Considered | # By Default Selection of Electric Motor Type will Be ODP. # By Default Selection of Starter Type will be DOL for motor rating upto 75 HP . Star Delta Open Transition type for motors ratings greater than 75 HP. # By Default Selection of Controllers Enclosure Rating will be Nema 2-IP31.
1 | Water Type | Fresh Water****
2 | Water Temperature | 5 to 49 Degree celsius
3 | Altitude | Upto 300 feet above Sea level****
4 | Ambient Temperature | 5 to 25 Degree Celsius
5 | Suction State | Totally Flooded Suction****
Notes:**** | For higher altitude & higher ambient temperatures- deration factors to be considered on drivers.
For lesser NPSHa with respect to NPSHr @ actual site conditions.
Sea water/Saline water/ water with higher TDS values.
For such cases please contact Wilo engineering for assistance